## HEADLOSS
WESTFALL MANUFACTURING CO.
[12 empty] | Min flow rate | Max Flow rate
HEADLOSS CHART | [11 empty] | 550.801 | 6609.612
pipe ID | 15 | inches
Pipe area | 1.2272 | ft2 |  |  |  | MODEL 2800 | MODEL 2800 | MODEL 2800 | MODEL 3050 | MODEL 3050 | MODEL 3050
|  |  | 0.7 BETA | 0.8 BETA | 0.9 BETA | 0.7 BETA | 0.8 BETA | 0.9 BETA | SINGLE | DOUBLE | TRIPLE
GPM | CFS | ft/s | ft head loss | ft head loss | ft head loss | psi Head loss | psi Head loss | psi Head loss | psi Head loss | psi Head loss | psi Head loss
550.801 | 1.2272 | 1 | 0.50606 | 0.21165 | 0.10533 | 0.21917 | 0.091665 | 0.045617 | 0.0037459 | 0.0075995 | 0.011029 |  | * PLEASE ENTER PIPE ID IN INCHES
1101.602 | 2.4544 | 2 | 2.0242 | 0.84658 | 0.4213 | 0.8767 | 0.36666 | 0.18247 | 0.014984 | 0.030398 | 0.044117
1652.403 | 3.6816 | 3 | 4.5545 | 1.9048 | 0.94793 | 1.9726 | 0.82498 | 0.41055 | 0.033713 | 0.068395 | 0.099264
2203.204 | 4.9087 | 4 | 8.0969 | 3.3863 | 1.6852 | 3.5068 | 1.4666 | 0.72987 | 0.059935 | 0.12159 | 0.17647
2754.005 | 6.1359 | 5 | 12.6514 | 5.2911 | 2.6332 | 5.4794 | 2.2916 | 1.1404 | 0.093648 | 0.18999 | 0.27573
3304.806 | 7.3631 | 6 | 18.218 | 7.6193 | 3.7917 | 7.8903 | 3.2999 | 1.6422 | 0.13485 | 0.27358 | 0.39706
3855.607 | 8.5903 | 7 | 24.7967 | 10.3707 | 5.161 | 10.7395 | 4.4916 | 2.2352 | 0.18355 | 0.37237 | 0.54044
4406.408 | 9.8175 | 8 | 32.3876 | 13.5453 | 6.7409 | 14.0272 | 5.8665 | 2.9195 | 0.23974 | 0.48637 | 0.70588
4957.209 | 11.0447 | 9 | 40.9905 | 17.1433 | 8.5314 | 17.7531 | 7.4248 | 3.695 | 0.30342 | 0.61556 | 0.89338
5508.01 | 12.2718 | 10 | 50.6056 | 21.1646 | 10.5326 | 21.9174 | 9.1665 | 4.5617 | 0.37459 | 0.75995 | 1.1029
6058.811 | 13.499 | 11 | 61.2328 | 25.6092 | 12.7445 | 26.5201 | 11.0914 | 5.5197 | 0.45326 | 0.91954 | 1.3345
6609.612 | 14.7262 | 12 | 72.872 | 30.477 | 15.167 | 31.5611 | 13.1997 | 6.5689 | 0.53941 | 1.0943 | 1.5882
7160.413 | 15.9534 | 13 | 85.5234 | 35.7682 | 17.8001 | 37.0405 | 15.4913 | 7.7093 | 0.63306 | 1.2843 | 1.864
7711.214 | 17.1806 | 14 | 99.187 | 41.4826 | 20.6439 | 42.9582 | 17.9662 | 8.9409 | 0.7342 | 1.4895 | 2.1617
8262.015 | 18.4078 | 15 | 113.8626 | 47.6203 | 23.6984 | 49.3142 | 20.6245 | 10.2638 | 0.84284 | 1.7099 | 2.4816
pipe ID | 381 | mm |  |  |  | 0.7 BETA | 0.8 BETA | 0.9 BETA | MODEL 3050 | MODEL 3050 | MODEL 3050
Pipe area | 0.11401 | m2 | 0.7 BETA | 0.8 BETA | 0.9 BETA | kg/cm2 | kg/cm2 | kg/cm2 | SINGLE | DOUBLE | TRIPLE
m3/hr | m3/s | m/s | m head loss | m head loss | m head loss | head loss | head loss | head loss | kg/cm2 | kg/cm2 | kg/cm2
125.0869 | 0.034746 | 0.30477 | 0.15444 | 0.064592 | 0.03213 | 0.015429 | 0.0064528 | 0.0032099 | 0.0002637 | 0.00053498 | 0.00077642
250.1738 | 0.069493 | 0.60954 | 0.61777 | 0.25837 | 0.12852 | 0.061716 | 0.025811 | 0.012839 | 0.0010548 | 0.0021399 | 0.0031057
375.2607 | 0.10424 | 0.9143 | 1.39 | 0.58133 | 0.28917 | 0.13886 | 0.058076 | 0.028889 | 0.0023733 | 0.0048148 | 0.0069878
500.3476 | 0.13899 | 1.2191 | 2.4711 | 1.0335 | 0.51408 | 0.24687 | 0.10325 | 0.051358 | 0.0042192 | 0.0085596 | 0.012423
625.4345 | 0.17373 | 1.5238 | 3.8611 | 1.6148 | 0.80325 | 0.38573 | 0.16132 | 0.080246 | 0.0065925 | 0.013374 | 0.019411
750.5214 | 0.20848 | 1.8286 | 5.5599 | 2.3253 | 1.1567 | 0.55545 | 0.2323 | 0.11555 | 0.0094932 | 0.019259 | 0.027951
875.6084 | 0.24322 | 2.1334 | 7.5677 | 3.165 | 1.5744 | 0.75602 | 0.31619 | 0.15728 | 0.012921 | 0.026214 | 0.038045
1000.6953 | 0.27797 | 2.4381 | 9.8843 | 4.1339 | 2.0563 | 0.98746 | 0.41298 | 0.20543 | 0.016877 | 0.034238 | 0.049691
1125.7822 | 0.31272 | 2.7429 | 12.5099 | 5.232 | 2.6025 | 1.2498 | 0.52268 | 0.26 | 0.02136 | 0.043333 | 0.06289
1250.8691 | 0.34746 | 3.0477 | 15.4443 | 6.4592 | 3.213 | 1.5429 | 0.64528 | 0.32099 | 0.02637 | 0.053498 | 0.077642
1375.956 | 0.38221 | 3.3524 | 18.6876 | 7.8156 | 3.8877 | 1.8669 | 0.78079 | 0.38839 | 0.031908 | 0.064732 | 0.093947
1501.0429 | 0.41696 | 3.6572 | 22.2397 | 9.3013 | 4.6267 | 2.2218 | 0.92921 | 0.46222 | 0.037973 | 0.077036 | 0.11181
1626.1298 | 0.4517 | 3.962 | 26.1008 | 10.9161 | 5.43 | 2.6075 | 1.0905 | 0.54246 | 0.044565 | 0.090411 | 0.13122
1751.2167 | 0.48645 | 4.2668 | 30.2708 | 12.66 | 6.2975 | 3.0241 | 1.2648 | 0.62913 | 0.051685 | 0.10486 | 0.15218
1876.3036 | 0.5212 | 4.5715 | 34.7496 | 14.5332 | 7.2293 | 3.4715 | 1.4519 | 0.72222 | 0.059333 | 0.12037 | 0.1747